## Sheet1
ALARMS.A001 | BOOL | TAH3101 Temperature high - Cabinet
ALARMS.A002 | BOOL | XA3101A Fuse failure - 230V
ALARMS.A003 | BOOL | XA3101B Fuse failure - 24V
ALARMS.A004 | BOOL | XA0123 Common alarm - Turbine overspeed protection
ALARMS.A005 | BOOL | XZ0122B Trip valve 2 off
ALARMS.A006 | BOOL | SA0121A Probe failure - SE0121A
ALARMS.A007 | BOOL | SA0122A Probe failure - SE0122A
ALARMS.A008 | BOOL | XA0138 MMS rack not OK
ALARMS.A009 | BOOL | XZ0122A Trip valve 1 off
ALARMS.A010 | BOOL | SA0122B Probe failure - SE0122B
ALARMS.A011 | BOOL | SA0121B Probe failure - SE0121B
ALARMS.A012 | BOOL | PAL2373 Pressure main steam supply low
ALARMS.A013 | BOOL | SA0122C Probe failure - SE0122C
ALARMS.A014 | BOOL | XZ0122C Trip valve 3 off
ALARMS.A015 | BOOL | ZA6182 Anti-surge valve solenoid deenergize by customer ESD
ALARMS.A016 | BOOL | PLC_ERR_EA PLC I/O error
ALARMS.A017 | BOOL | PLC_ERR_RED PLC redundancy error
ALARMS.A018 | BOOL | PLC_ERR_BAT PLC backup battery empty
ALARMS.A019 | BOOL | PLC_ERR_MDL PLC I/O module error/removed
ALARMS.A020 | BOOL | SIM_ACTIVE Simulation mode active
ALARMS.A021 | BOOL | E1651_1_ERR Speed module BRAUN E1651 channel 1 error
ALARMS.A022 | BOOL | E1651_2_ERR Speed module BRAUN E1651 channel 2 error
ALARMS.A023 | BOOL | E1651_3_ERR Speed module BRAUN E1651 channel 3 error
ALARMS.A024 | BOOL | E1651_4_ERR Speed module BRAUN E1651 channel 4 error
ALARMS.A025 | BOOL | HDP_MASYS_FLT PLC DP-Mastersystem redundancy failure
ALARMS.A026 | BOOL | HDP_STAT_FLT PLC DP-Station redundancy failure
ALARMS.A027 | BOOL | MMS_ERR MMS comm. - All conn. faulty
ALARMS.A028 | BOOL | MMS_ERR0A MMS comm. - Conn. fault 0A (S7-CP_0 <-> MMS-CP_A)
ALARMS.A029 | BOOL | MMS_ERR1B MMS comm. - Conn. fault 1B (S7-CP_1 <-> MMS-CP_B)
ALARMS.A030 | BOOL | DCS_ERR DCS comm. - All connectons faulty
ALARMS.A031 | BOOL | DCS_ERR0A DCS comm. - Conn. fault 0A (S7-CP_0 <-> DCS-CP_A)
ALARMS.A032 | BOOL | DCS_ERR1B DCS comm. - Conn. fault 1B (S7-CP_1 <-> DCS-CP_B)
ALARMS.A033 | BOOL | VXAH0148A Vibration compressor shaft rear high
ALARMS.A034 | BOOL | VXAHH0148A Vibration compressor shaft rear too high
ALARMS.A035 | BOOL | VXAH0144A Vibration turbine shaft front high
ALARMS.A036 | BOOL | VXAHH0144A Vibration turbine shaft front too high
ALARMS.A037 | BOOL | XALL0152 Position compressor shaft too low
ALARMS.A038 | BOOL | XAL0152 Position compressor shaft low
ALARMS.A039 | BOOL | XAH0152 Position compressor shaft high
ALARMS.A040 | BOOL | XAHH0152 Position compressor shaft too high
ALARMS.A041 | BOOL | XALL0141 Position turbine shaft front too low
ALARMS.A042 | BOOL | XAL0141 Position turbine shaft front low
ALARMS.A043 | BOOL | XAH0141 Position turbine shaft front high
ALARMS.A044 | BOOL | XAHH0141 Position turbine shaft front too high
ALARMS.A045 | BOOL | VYAH0148B Vibration compressor shaft DE high
ALARMS.A046 | BOOL | VYAHH0148B Vibration compressor shaft DE too high
ALARMS.A047 | BOOL | VYAH0144B Vibration turbine shaft front high
ALARMS.A048 | BOOL | VYAHH0144B Vibration turbine shaft front too high
ALARMS.A049 | BOOL | XALL0153 Position compressor shaft too low
ALARMS.A050 | BOOL | XAL0153 Position compressor shaft low
ALARMS.A051 | BOOL | XAH0153 Position compressor shaft high
ALARMS.A052 | BOOL | XAHH0153 Position compressor shaft too high
ALARMS.A053 | BOOL | XALL0142 Position turbine shaft front too low
ALARMS.A054 | BOOL | XAL0142 Position turbine shaft front low
ALARMS.A055 | BOOL | XAH0142 Position turbine shaft front high
ALARMS.A056 | BOOL | XAHH0142 Position turbine shaft front too high
ALARMS.A057 | BOOL | VXAH0150A Vibration compressor shaft NDE high
ALARMS.A058 | BOOL | VXAHH0150A Vibration compressor shaft NDE too high
ALARMS.A059 | BOOL | VXAH0146A Vibration turbine shaft rear high
ALARMS.A060 | BOOL | VXAHH0146A Vibration turbine shaft rear too high
ALARMS.A061 | BOOL | VYAH0150B Vibration compressor shaft NDE high
ALARMS.A062 | BOOL | VYAHH0150B Vibration compressor shaft NDE too high
ALARMS.A063 | BOOL | VYAH0146B Vibration turbine shaft rear high
ALARMS.A064 | BOOL | VYAHH0146B Vibration turbine shaft rear too high
ALARMS.A065 | BOOL | TAH1139 Temperature compressor radial bearing DE high
ALARMS.A066 | BOOL | TAHH1139 Temperature compressor radial bearing DE too high
ALARMS.A067 | BOOL | TAH1141 Temperature compressor radial bearing NDE high
ALARMS.A068 | BOOL | TAHH1141 Temperature compressor radial bearing NDE too high
ALARMS.A069 | BOOL | TAH1143 Temperature compressor axial bearing inside high
ALARMS.A070 | BOOL | TAHH1143 Temperature compressor axial bearing inside too high
ALARMS.A071 | BOOL | TAH1145 Temperature compressor axial bearing outside high
ALARMS.A072 | BOOL | TAHH1145 Temperature compressor axial bearing outside too high
ALARMS.A073 | BOOL | TAH1140 Temperature compressor radial bearing DE high
ALARMS.A074 | BOOL | TAHH1140 Temperature compressor radial bearing DE too high
ALARMS.A075 | BOOL | TAH1142 Temperature compressor radial bearing NDE high
ALARMS.A076 | BOOL | TAHH1142 Temperature compressor radial bearing NDE too high
ALARMS.A077 | BOOL | TAH1144 Temperature compressor axial bearing inside high
ALARMS.A078 | BOOL | TAHH1144 Temperature compressor axial bearing inside too high
ALARMS.A079 | BOOL | TAH1146 Temperature compressor axial bearing outside high
ALARMS.A080 | BOOL | TAHH1146 Temperature compressor axial bearing outside too high
ALARMS.A081 | BOOL | TAH1135 Temperature turbine radial bearing front high
ALARMS.A082 | BOOL | TAH1137 Temperature turbine radial bearing rear high
ALARMS.A083 | BOOL | TAH1131 Temperature turbine axial bearing inside high
ALARMS.A084 | BOOL | TAH1133 Temperature turbine axial bearing outside high
ALARMS.A085 | BOOL | TAH1136 Temperature turbine radial bearing front high
ALARMS.A086 | BOOL | TAH1138 Temperature turbine radial bearing rear high
ALARMS.A087 | BOOL | TAH1132 Temperature turbine axial bearing inside high
ALARMS.A088 | BOOL | TAH1134 Temperature turbine axial bearing outside high
ALARMS.A089 | BOOL | FI3068_ERR Diff.-Pressure - Compressor suction 1st process stage
ALARMS.A090 | BOOL | PI2075A_ERR Pressure - Compressor suction 1st process stage
ALARMS.A091 | BOOL | PI2075B_ERR Pressure - Compressor discharge 1st process stage
ALARMS.A092 | BOOL | SC0121SP_ERR Turbine speed controller setpoint (70%-105%) from DCS
ALARMS.A093 | BOOL | ZI6182_ERR Position feedback - Anti-surge valve
ALARMS.A094 | BOOL | TI1182_ERR Temperature - Compressor suction 1st process stage
ALARMS.A095 | BOOL | TI1383_ERR Temperature - Compressor discharge 1st process stage
ALARMS.A096 | BOOL | ZI6122_ERR Position feedback - Main steam control valve
ALARMS.A097 | BOOL | VXI0148A_ERR Vibration compressor shaft rear
ALARMS.A098 | BOOL | VXI0144A_ERR Vibration turbine shaft front
ALARMS.A099 | BOOL | XI0152_ERR Position compressor shaft
ALARMS.A100 | BOOL | XI0141_ERR Position turbine shaft front
ALARMS.A101 | BOOL | VYI0148B_ERR Vibration compressor shaft DE
ALARMS.A102 | BOOL | VYI0144B_ERR Vibration turbine shaft front
ALARMS.A103 | BOOL | XI0153_ERR Position compressor shaft
ALARMS.A104 | BOOL | XI0142_ERR Position turbine shaft front
ALARMS.A105 | BOOL | VXI0150A_ERR Vibration compressor shaft NDE
ALARMS.A106 | BOOL | VXI0146A_ERR Vibration turbine shaft rear
ALARMS.A107 | BOOL | VYI0150B_ERR Vibration compressor shaft NDE
ALARMS.A108 | BOOL | VYI0146B_ERR Vibration turbine shaft rear
ALARMS.A109 | BOOL | TI1139_ERR Temperature compressor radial bearing DE
ALARMS.A110 | BOOL | TI1141_ERR Temperature compressor radial bearing NDE
ALARMS.A111 | BOOL | TI1143_ERR Temperature compressor axial bearing inside
ALARMS.A112 | BOOL | TI1145_ERR Temperature compressor axial bearing outside
ALARMS.A113 | BOOL | TI1140_ERR Temperature compressor radial bearing DE
ALARMS.A114 | BOOL | TI1142_ERR Temperature compressor radial bearing NDE
ALARMS.A115 | BOOL | TI1144_ERR Temperature compressor axial bearing inside
ALARMS.A116 | BOOL | TI1146_ERR Temperature compressor axial bearing outside
ALARMS.A117 | BOOL | TI1135_ERR Temperature turbine radial bearing front
ALARMS.A118 | BOOL | TI1137_ERR Temperature turbine radial bearing rear
ALARMS.A119 | BOOL | TI1131_ERR Temperature turbine axial bearing inside
ALARMS.A120 | BOOL | TI1133_ERR Temperature turbine axial bearing outside
ALARMS.A121 | BOOL | TI1136_ERR Temperature turbine radial bearing front
ALARMS.A122 | BOOL | TI1138_ERR Temperature turbine radial bearing rear
ALARMS.A123 | BOOL | TI1132_ERR Temperature turbine axial bearing inside
ALARMS.A124 | BOOL | TI1134_ERR Temperature turbine axial bearing outside
ALARMS.A125 | BOOL | KI0143_ERR Speed turbine shaft keyphasor
TRIPS.T001 | BOOL | HZ0158 Emergency shutdown push button UCP
TRIPS.T002 | BOOL | XAHH0151 Common trip shaft vibration
TRIPS.T003 | BOOL | XAHH0155 Common trip shaft position
TRIPS.T004 | BOOL | XAHH0156 Common trip MMS probe failure
TRIPS.T005 | BOOL | XAHH0157 Common trip bearing temperature
TRIPS.T006 | BOOL | XZ0159 Startup condition faulty Start-up interlock from DCS
TRIPS.T007 | BOOL | ZAH6182 Startup condition faulty Anti-surge valve not open
TRIPS.T008 | BOOL | TR_ACC_L Turbine low acceleration in critical speed zone trip
TRIPS.T009 | BOOL | TR_OVERSPEED Turbine overspeed limit exceeded (SCAUT)
TRIPS.T010 | BOOL | XZ9150 Turbine rotor sticking protection trip
TRIPS.T011 | BOOL | TR_F_TIMER Turbine speed measurement fail safe timer trip
TRIPS.T012 | BOOL | XZA0122 Trip by ESD, BRAUN or multiple fuse faillure
TRIPS.T013 | BOOL | TR_SP_MEAS Turbine trip by speed measurement error
TRIPS.T014 | BOOL | TR_OVSP_PROT Turbine overspeed limit exceeded BRAUN
TRIPS.T015 | BOOL | TR_MAN_MON Manual shutdown (monitor)
TRIPS.T016 | BOOL | TR_START_MONIT Turbine startup time monitoring speed below min. govenor speed
TRIPS.T017 | BOOL | TR_MIN_SPEED_1 Turbine underspeed trip (Limit 1)
TRIPS.T018 | BOOL | VAHH1418C Vibration compressor shaft too high (2oo4)
TRIPS.T019 | BOOL | VZAHH0152C Position compressor shaft too high (2oo2)
TRIPS.T020 | BOOL | VZALL0152C Position compressor shaft too low (2oo2)
TRIPS.T021 | BOOL | TAHH1140C Temperature compressor radial bearing DE too high (2oo2)
TRIPS.T022 | BOOL | TAHH1142C Temperature compressor radial bearing NDE too high (2oo2)
TRIPS.T023 | BOOL | TAHH1144C Temperature compressor axial bearing inside too high (2oo2)
TRIPS.T024 | BOOL | TAHH1146C Temperature compressor axial bearing outside too high (2oo2)
TRIPS.T025 | BOOL | VI1418C_ERR Vibration compressor shaft probe failure (2oo4)
TRIPS.T026 | BOOL | TI1140C_ERR Temperature compressor radial bearing DE probe failure (2oo2)
TRIPS.T027 | BOOL | TI1142C_ERR Temperature compressor radial bearing NDE probe failure (2oo2)
TRIPS.T028 | BOOL | TI1144C_ERR Temperature compressor axial bearing inside probe failure (2oo2)
TRIPS.T029 | BOOL | TI1146C_ERR Temperature compressor axial bearing outside probe failure (2oo2)
TRIPS.T030 | BOOL | VAHH0144 Vibration turbine shaft too high (2oo4)
TRIPS.T031 | BOOL | VZAHH0141A Position turbine shaft front too high (2oo2)
TRIPS.T032 | BOOL | VZALL0141A Position turbine shaft front too low (2oo2)
TRIPS.T033 | BOOL | VI0144_ERR Vibration turbine shaft probe failure (2oo4)
TRIPS.T034 | BOOL | TI1136C_ERR Temperature turbine radial bearing front probe failure (1oo2)
TRIPS.T035 | BOOL | TI1138C_ERR Temperature turbine radial bearing rear probe failure (1oo2)
TRIPS.T036 | BOOL | TI1132C_ERR Temperature turbine axial bearing inside probe failure (1oo2)
TRIPS.T037 | BOOL | TI1134C_ERR Temperature turbine axial bearing outside probe failure (1oo2)
TRIPS.T038 | BOOL | TAH1135_SC Startup condition faulty Temperature turbine radial bearing front h
TRIPS.T039 | BOOL | TAH1136_SC Startup condition faulty Temperature turbine radial bearing front h
TRIPS.T040 | BOOL | TAH1137_SC Startup condition faulty Temperature turbine radial bearing rear hi
TRIPS.T041 | BOOL | TAH1138_SC Startup condition faulty Temperature turbine radial bearing rear hi
TRIPS.T042 | BOOL | TAHH1135 Temperature turbine radial bearing front too high
TRIPS.T043 | BOOL | TAHH1137 Temperature turbine radial bearing rear too high
TRIPS.T044 | BOOL | TAHH1131 Temperature turbine axial bearing inside too high
TRIPS.T045 | BOOL | TAHH1133 Temperature turbine axial bearing outside too high
TRIPS.T046 | BOOL | TAHH1136 Temperature turbine radial bearing front too high
TRIPS.T047 | BOOL | TAHH1138 Temperature turbine radial bearing rear too high
TRIPS.T048 | BOOL | TAHH1132 Temperature turbine axial bearing inside too high
TRIPS.T049 | BOOL | TAHH1134 Temperature turbine axial bearing outside too high
TRIPS.T050 | BOOL | TAHH1131C Temperature turbine axial bearing inside too high
TRIPS.T051 | BOOL | TAHH1133C Temperature turbine axial bearing outside too high
TRIPS.T052 | BOOL | TAHH1135C Temperature turbine radial bearing front too high
TRIPS.T053 | BOOL | TAHH1137C Temperature turbine radial bearing rear too high