## Sheet1
ALARMS.A001 | BOOL | TAH4101 Cabinet temperature high
ALARMS.A002 | BOOL | XA4101A 220V AC Fuse failure
ALARMS.A003 | BOOL | XA4101B 24V DC Fuse failure
ALARMS.A004 | BOOL | XAH21030 Converter Alarm from VFD
ALARMS.A005 | BOOL | VA9040A MMS rack 1 not ok
ALARMS.A006 | BOOL | VA9040B MMS rack 2 not ok
ALARMS.A007 | BOOL | PLC_ERR_EA PLC I/O error
ALARMS.A008 | BOOL | PLC_ERR_RED PLC redundancy error
ALARMS.A009 | BOOL | PLC_ERR_BAT PLC backup battery empty
ALARMS.A010 | BOOL | PLC_ERR_MDL PLC I/O module error/removed
ALARMS.A011 | BOOL | SIM_ACTIVE Simulation mode active
ALARMS.A012 | BOOL | HDP_MASYS_FLT PLC DP-Mastersystem redundancy failure
ALARMS.A013 | BOOL | HDP_STAT_FLT PLC DP-Station redundancy failure
ALARMS.A014 | BOOL | MMS_ERR MMS Rack 1 comm. - All conn. faulty
ALARMS.A015 | BOOL | MMS_ERR0A MMS Rack 1 comm. - Conn. fault 0A (S7-CP_0 <-> MMS-CP_A)
ALARMS.A016 | BOOL | MMS_ERR1B MMS Rack 1 comm. - Conn. fault 1B (S7-CP_1 <-> MMS-CP_B)
ALARMS.A017 | BOOL | MMS2_ERR MMS Rack 2 comm. - All conn. faulty
ALARMS.A018 | BOOL | MMS2_ERR0A MMS Rack 2 comm. - Conn. fault 0A (S7-CP_0 <-> MMS-CP_A)
ALARMS.A019 | BOOL | MMS2_ERR1B MMS Rack 2 comm. - Conn. fault 1B (S7-CP_1 <-> MMS-CP_B)
ALARMS.A020 | BOOL | DCS_ERR DCS comm. - All connections faulty
ALARMS.A021 | BOOL | DCS_ERR0A DCS comm. - Conn. fault 0A (S7-CP_0 <-> DCS-CP_A)
ALARMS.A022 | BOOL | DCS_ERR1B DCS comm. - Conn. fault 1B (S7-CP_1 <-> DCS-CP_B)
ALARMS.A023 | BOOL | VAH0054X Vibration gearbox LS shaft NDE high
ALARMS.A024 | BOOL | VAH0056X Vibration gearbox LS shaft DE high
ALARMS.A025 | BOOL | VAH0058X Vibration compressor shaft NDE high
ALARMS.A026 | BOOL | VAHH0058X Vibration compressor shaft NDE too high
ALARMS.A027 | BOOL | VAH0057X Vibration compressor shaft DE high
ALARMS.A028 | BOOL | VAHH0057X Vibration compressor shaft DE too high
ALARMS.A029 | BOOL | VAH0054Y Vibration gearbox LS shaft NDE high
ALARMS.A030 | BOOL | VAH0056Y Vibration gearbox LS shaft DE high
ALARMS.A031 | BOOL | VAH0058Y Vibration compressor shaft NDE high
ALARMS.A032 | BOOL | VAHH0058Y Vibration compressor shaft NDE too high
ALARMS.A033 | BOOL | VAH0057Y Vibration compressor shaft DE high
ALARMS.A034 | BOOL | VAHH0057Y Vibration compressor shaft DE too high
ALARMS.A035 | BOOL | VAH0061X Vibration motor shaft NDE high
ALARMS.A036 | BOOL | VAH0062X Vibration motor shaft DE high
ALARMS.A037 | BOOL | VAH0050X Vibration gearbox HS shaft DE high
ALARMS.A038 | BOOL | VAH0051X Vibration gearbox HS shaft NDE high
ALARMS.A039 | BOOL | VAH0061Y Vibration motor shaft NDE high
ALARMS.A040 | BOOL | VAH0062Y Vibration motor shaft DE high
ALARMS.A041 | BOOL | VALL0060AZ Position compressor shaft NDE too low
ALARMS.A042 | BOOL | VAL0060AZ Position compressor shaft NDE low
ALARMS.A043 | BOOL | VAH0060AZ Position compressor shaft NDE high
ALARMS.A044 | BOOL | VAHH0060AZ Position compressor shaft NDE too high
ALARMS.A045 | BOOL | VALL0052AZ Position gearbox LS shaft NDE too low
ALARMS.A046 | BOOL | VAL0052AZ Position gearbox LS shaft NDE low
ALARMS.A047 | BOOL | VAH0052AZ Position gearbox LS shaft NDE high
ALARMS.A048 | BOOL | VAHH0052AZ Position gearbox LS shaft NDE too high
ALARMS.A049 | BOOL | VALL0060BZ Position compressor shaft NDE too low
ALARMS.A050 | BOOL | VAL0060BZ Position compressor shaft NDE low
ALARMS.A051 | BOOL | VAH0060BZ Position compressor shaft NDE high
ALARMS.A052 | BOOL | VAHH0060BZ Position compressor shaft NDE too high
ALARMS.A053 | BOOL | VALL0052BZ Position gearbox LS shaft NDE too low
ALARMS.A054 | BOOL | VAL0052BZ Position gearbox LS shaft NDE low
ALARMS.A055 | BOOL | VAH0052BZ Position gearbox LS shaft NDE high
ALARMS.A056 | BOOL | VAHH0052BZ Position gearbox LS shaft NDE too high
ALARMS.A057 | BOOL | VAH0050Y Vibration gearbox HS shaft DE high
ALARMS.A058 | BOOL | VAH0051Y Vibration gearbox HS shaft NDE high
ALARMS.A059 | BOOL | VAH0055 Acceleration gearbox casing high
ALARMS.A060 | BOOL | TAH1451 Temperature compressor radial bearing NDE high
ALARMS.A061 | BOOL | TAHH1451 Temperature compressor radial bearing NDE too high
ALARMS.A062 | BOOL | TAH1453 Temperature compressor axial bearing inside NDE high
ALARMS.A063 | BOOL | TAHH1453 Temperature compressor axial bearing inside NDE too high
ALARMS.A064 | BOOL | TAH1455 Temperature compressor axial bearing outside NDE high
ALARMS.A065 | BOOL | TAHH1455 Temperature compressor axial bearing outside NDE too high
ALARMS.A066 | BOOL | TAH1457 Temperature compressor radial bearing DE high
ALARMS.A067 | BOOL | TAHH1457 Temperature compressor radial bearing DE too high
ALARMS.A068 | BOOL | TAH1452 Temperature compressor radial bearing NDE high
ALARMS.A069 | BOOL | TAHH1452 Temperature compressor radial bearing NDE too high
ALARMS.A070 | BOOL | TAH1454 Temperature compressor axial bearing inside NDE high
ALARMS.A071 | BOOL | TAHH1454 Temperature compressor axial bearing inside NDE too high
ALARMS.A072 | BOOL | TAH1456 Temperature compressor axial bearing outside NDE high
ALARMS.A073 | BOOL | TAHH1456 Temperature compressor axial bearing outside NDE too high
ALARMS.A074 | BOOL | TAH1458 Temperature compressor radial bearing DE high
ALARMS.A075 | BOOL | TAHH1458 Temperature compressor radial bearing DE too high
ALARMS.A076 | BOOL | TAH1459 Temperature gearbox LS shaft radial bearing NDE high
ALARMS.A077 | BOOL | TAHH1459 Temperature gearbox LS shaft radial bearing NDE too high
ALARMS.A078 | BOOL | TAH1461 Temperature gearbox LS shaft axial bearing inside NDE high
ALARMS.A079 | BOOL | TAHH1461 Temperature gearbox LS shaft axial bearing inside NDE too high
ALARMS.A080 | BOOL | TAH1463 Temperature gearbox LS shaft axial bearing outside NDE high
ALARMS.A081 | BOOL | TAHH1463 Temperature gearbox LS shaft axial bearing outside NDE too high
ALARMS.A082 | BOOL | TAH1465 Temperature gearbox LS shaft radial bearing DE high
ALARMS.A083 | BOOL | TAHH1465 Temperature gearbox LS shaft radial bearing DE too high
ALARMS.A084 | BOOL | TAH1460 Temperature gearbox LS shaft radial bearing NDE high
ALARMS.A085 | BOOL | TAHH1460 Temperature gearbox LS shaft radial bearing NDE too high
ALARMS.A086 | BOOL | TAH1462 Temperature gearbox LS shaft axial bearing inside NDE high
ALARMS.A087 | BOOL | TAHH1462 Temperature gearbox LS shaft axial bearing inside NDE too high
ALARMS.A088 | BOOL | TAH1464 Temperature gearbox LS shaft axial bearing outside NDE high
ALARMS.A089 | BOOL | TAHH1464 Temperature gearbox LS shaft axial bearing outside NDE too high
ALARMS.A090 | BOOL | TAH1466 Temperature gearbox LS shaft radial bearing DE high
ALARMS.A091 | BOOL | TAHH1466 Temperature gearbox LS shaft radial bearing DE too high
ALARMS.A092 | BOOL | TAH1467 Temperature gearbox HS shaft radial bearing DE high
ALARMS.A093 | BOOL | TAHH1467 Temperature gearbox HS shaft radial bearing DE too high
ALARMS.A094 | BOOL | TAH1469 Temperature gearbox HS shaft radial bearing NDE high
ALARMS.A095 | BOOL | TAHH1469 Temperature gearbox HS shaft radial bearing NDE too high
ALARMS.A096 | BOOL | TAH1476 Temperature motor shaft radial bearing DE high
ALARMS.A097 | BOOL | TAH1474 Temperature motor hot air high
ALARMS.A098 | BOOL | TAH1468 Temperature gearbox HS shaft radial bearing DE high
ALARMS.A099 | BOOL | TAHH1468 Temperature gearbox HS shaft radial bearing DE too high
ALARMS.A100 | BOOL | TAH1470 Temperature gearbox HS shaft radial bearing NDE high
ALARMS.A101 | BOOL | TAHH1470 Temperature gearbox HS shaft radial bearing NDE too high
ALARMS.A102 | BOOL | TAH1477 Temperature motor shaft radial bearing NDE high
ALARMS.A103 | BOOL | TAH1475 Temperature motor cold air high
ALARMS.A104 | BOOL | TAH1471 Temperature motor winding U high
ALARMS.A105 | BOOL | TAH1472 Temperature motor winding V high
ALARMS.A106 | BOOL | TAH1473 Temperature motor winding W high
ALARMS.A107 | BOOL | FI3127_ERR Flow - Compr. 1st stage suction
ALARMS.A108 | BOOL | PI2284_ERR Pressure - Compr. 1st stage suction
ALARMS.A109 | BOOL | PI2283_ERR Pressure - Compr. 2nd stage discharge
ALARMS.A110 | BOOL | ZI3127_ERR Position - AS valve recycle line compr.
ALARMS.A111 | BOOL | TI1483_ERR Temperature - Compr. 2nd stage discharge
ALARMS.A112 | BOOL | TI1482_ERR Temperature - Compr. 1st stage suction
ALARMS.A113 | BOOL | SI21028_ERR Speed main motor actual value from VFD
ALARMS.A114 | BOOL | VI0054X_ERR Vibration gearbox LS shaft NDE
ALARMS.A115 | BOOL | VI0056X_ERR Vibration gearbox LS shaft DE
ALARMS.A116 | BOOL | VI0058X_ERR Vibration compressor shaft NDE
ALARMS.A117 | BOOL | VI0057X_ERR Vibration compressor shaft DE
ALARMS.A118 | BOOL | VI0054Y_ERR Vibration gearbox LS shaft NDE
ALARMS.A119 | BOOL | VI0056Y_ERR Vibration gearbox LS shaft DE
ALARMS.A120 | BOOL | VI0058Y_ERR Vibration compressor shaft NDE
ALARMS.A121 | BOOL | VI0057Y_ERR Vibration compressor shaft DE
ALARMS.A122 | BOOL | VI0061X_ERR Vibration motor shaft NDE
ALARMS.A123 | BOOL | VI0062X_ERR Vibration motor shaft DE
ALARMS.A124 | BOOL | VI0050X_ERR Vibration gearbox HS shaft DE
ALARMS.A125 | BOOL | VI0051X_ERR Vibration gearbox HS shaft NDE
ALARMS.A126 | BOOL | VI0060AZ_ERR Position compressor shaft NDE
ALARMS.A127 | BOOL | VI0052AZ_ERR Position gearbox LS shaft NDE
ALARMS.A128 | BOOL | VI0061Y_ERR Vibration motor shaft NDE
ALARMS.A129 | BOOL | VI0062Y_ERR Vibration motor shaft DE
ALARMS.A130 | BOOL | VI0060BZ_ERR Position compressor shaft NDE
ALARMS.A131 | BOOL | VI0052BZ_ERR Position gearbox LS shaft NDE
ALARMS.A132 | BOOL | VI0050Y_ERR Vibration gearbox HS shaft DE
ALARMS.A133 | BOOL | VI0051Y_ERR Vibration gearbox HS shaft NDE
ALARMS.A134 | BOOL | VI0055_ERR Acceleration gearbox casing
ALARMS.A135 | BOOL | VI0053_ERR Speed gearbox LS shaft keyphasor
ALARMS.A136 | BOOL | VI0059_ERR Speed compressor shaft NDE
ALARMS.A137 | BOOL | TI1451_ERR Temperature compressor radial bearing NDE
ALARMS.A138 | BOOL | TI1453_ERR Temperature compressor axial bearing inside NDE
ALARMS.A139 | BOOL | TI1455_ERR Temperature compressor axial bearing outside NDE
ALARMS.A140 | BOOL | TI1457_ERR Temperature compressor radial bearing DE
ALARMS.A141 | BOOL | TI1452_ERR Temperature compressor radial bearing NDE
ALARMS.A142 | BOOL | TI1454_ERR Temperature compressor axial bearing inside NDE
ALARMS.A143 | BOOL | TI1456_ERR Temperature compressor axial bearing outside NDE
ALARMS.A144 | BOOL | TI1458_ERR Temperature compressor radial bearing DE
ALARMS.A145 | BOOL | TI1459_ERR Temperature gearbox LS shaft radial bearing NDE
ALARMS.A146 | BOOL | TI1461_ERR Temperature gearbox LS shaft axial bearing inside NDE
ALARMS.A147 | BOOL | TI1463_ERR Temperature gearbox LS shaft axial bearing outside NDE
ALARMS.A148 | BOOL | TI1465_ERR Temperature gearbox LS shaft radial bearing DE
ALARMS.A149 | BOOL | TI1460_ERR Temperature gearbox LS shaft radial bearing NDE
ALARMS.A150 | BOOL | TI1462_ERR Temperature gearbox LS shaft axial bearing inside NDE
ALARMS.A151 | BOOL | TI1464_ERR Temperature gearbox LS shaft axial bearing outside NDE
ALARMS.A152 | BOOL | TI1466_ERR Temperature gearbox LS shaft radial bearing DE
ALARMS.A153 | BOOL | TI1467_ERR Temperature gearbox HS shaft radial bearing DE
ALARMS.A154 | BOOL | TI1469_ERR Temperature gearbox HS shaft radial bearing NDE
ALARMS.A155 | BOOL | TI1476_ERR Temperature motor shaft radial bearing DE
ALARMS.A156 | BOOL | TI1474_ERR Temperature motor hot air
ALARMS.A157 | BOOL | TI1468_ERR Temperature gearbox HS shaft radial bearing DE
ALARMS.A158 | BOOL | TI1470_ERR Temperature gearbox HS shaft radial bearing NDE
ALARMS.A159 | BOOL | TI1477_ERR Temperature motor shaft radial bearing NDE
ALARMS.A160 | BOOL | TI1475_ERR Temperature motor cold air
ALARMS.A161 | BOOL | TI1471_ERR Temperature motor winding U
ALARMS.A162 | BOOL | TI1472_ERR Temperature motor winding V
ALARMS.A163 | BOOL | TI1473_ERR Temperature motor winding W
ALARMS.A164 | BOOL | SI71009A_ERR Speed main motor setpoint from DCS (70-105% rated)
TRIPS.T001 | BOOL | XAHH21024 Converter Trip from VFD
TRIPS.T002 | BOOL | XA21029 Emergency Stop Converter
TRIPS.T003 | BOOL | HZ9030 ESD push button UCP
TRIPS.T004 | BOOL | XA21022 Startup condition faulty VFD not ready to power up
TRIPS.T005 | BOOL | ZAH3127 Startup condition faulty Anti-surge valve not open
TRIPS.T006 | BOOL | DCS_RLS Startup condition faulty Startup from DCS not released
TRIPS.T007 | BOOL | TR_MAN_MON Manual shutdown (monitor)
TRIPS.T008 | BOOL | TR_TRAIN_LOC Emercengy stop - Train trip local
TRIPS.T009 | BOOL | TR_TRAIN_DCS Emercengy stop - Train trip DCS
TRIPS.T010 | BOOL | VAHH1419 Vibration compressor shaft (2oo4)
TRIPS.T011 | BOOL | VAHH0060 Position compressor shaft NDE too high (2oo2)
TRIPS.T012 | BOOL | VALL0060 Position compressor shaft NDE too low (2oo2)
TRIPS.T013 | BOOL | VAHH0052 Position gearbox LS shaft NDE too high (2oo2)
TRIPS.T014 | BOOL | VALL0052 Position gearbox LS shaft NDE too low (2oo2)
TRIPS.T015 | BOOL | TAHH1452C Temperature compressor radial bearing NDE too high (2oo2)
TRIPS.T016 | BOOL | TAHH1454C Temperature compressor axial bearing inside NDE too high (2oo2)
TRIPS.T017 | BOOL | TAHH1456C Temperature compressor or axial bearing outside NDE too high (2oo2)
TRIPS.T018 | BOOL | TAHH1458C Temperature compressor radial bearing DE too high (2oo2)
TRIPS.T019 | BOOL | TAHH1459C Temperature gearbox LS shaft radial bearing NDE too high (2oo2)
TRIPS.T020 | BOOL | TAHH1461C Temperature gearbox LS shaft axial bearing inside NDE too high (2oo2
TRIPS.T021 | BOOL | TAHH1463C Temperature gearbox LS shaft axial bearing outside NDE too high (2oo
TRIPS.T022 | BOOL | TAHH1465C Temperature gearbox LS shaft radial bearing DE too high (2oo2)
TRIPS.T023 | BOOL | VI1419_ERR Vibration compressor shaft probe failure (2oo4)
TRIPS.T024 | BOOL | VI0054X_ERR Vibration gearbox LS shaft NDE probe failure (2oo2)
TRIPS.T025 | BOOL | VI0056_ERR Vibration gearbox LS shaft DE probe failure (2oo2)
TRIPS.T026 | BOOL | VI0050_ERR Vibration gearbox HS shaft DE probe failure (2oo2)
TRIPS.T027 | BOOL | VI0051_ERR Vibration gearbox HS shaft NDE probe failure (2oo2)
TRIPS.T028 | BOOL | VI0061_ERR Vibration motor shaft NDE probe failure (2oo2)
TRIPS.T029 | BOOL | VI0062_ERR Vibration motor shaft DE probe failure (2oo2)
TRIPS.T030 | BOOL | TI1452C_ERR Temperature compressor radial bearing NDE probe failure (2oo2)
TRIPS.T031 | BOOL | TI1454C_ERR Temperature compressor axial bearing inside NDE probe failure (2oo
TRIPS.T032 | BOOL | TI1456C_ERR Temperature compressor axial bearing outside NDE probe failure (2o
TRIPS.T033 | BOOL | TI1458C_ERR Temperature compressor radial bearing DE probe failure (2oo2)
TRIPS.T034 | BOOL | TI1459C_ERR Temperature gearbox LS shaft radial bearing NDE probe failure (2oo
TRIPS.T035 | BOOL | TI1461C_ERR Temperature gearbox LS shaft axial bearing inside NDE probe failur
TRIPS.T036 | BOOL | TI1463C_ERR Temperature gearbox LS shaft axial bearing outside NDE probe failu
TRIPS.T037 | BOOL | TI1465C_ERR Temperature gearbox LS shaft radial bearing DE probe failure (2oo2
TRIPS.T038 | BOOL | TI1467C_ERR Temperature gearbox HS shaft radial bearing DE probe failure (2oo2
TRIPS.T039 | BOOL | TI1469C_ERR Temperature gearbox HS shaft radial bearing NDE probe failure (2oo
TRIPS.T040 | BOOL | TAHH1467C Temperature gearbox HS shaft radial bearing DE too high (2oo2)
TRIPS.T041 | BOOL | TAHH1469C Temperature gearbox HS shaft radial bearing NDE too high (2oo2)
TRIPS.T042 | BOOL | XA1481 Main motor feedback error
TRIPS.T043 | BOOL | XA21027 Drive rotates from VFD drop off
TRIPS.T044 | BOOL | HZA9032 Trip from ESD system
TRIPS.T045 | BOOL | XZA9188 Trip safety relay UCP
TRIPS.T046 | BOOL | VAHH0054X Vibration gearbox LS shaft NDE too high
TRIPS.T047 | BOOL | VAHH0056X Vibration gearbox LS shaft DE too high
TRIPS.T048 | BOOL | VAHH0054Y Vibration gearbox LS shaft NDE too high
TRIPS.T049 | BOOL | VAHH0056Y Vibration gearbox LS shaft DE too high
TRIPS.T050 | BOOL | VAHH0061X Vibration motor shaft NDE too high
TRIPS.T051 | BOOL | VAHH0062X Vibration motor shaft DE too high
TRIPS.T052 | BOOL | VAHH0050X Vibration gearbox HS shaft DE too high
TRIPS.T053 | BOOL | VAHH0051X Vibration gearbox HS shaft NDE too high
TRIPS.T054 | BOOL | VAHH0061Y Vibration motor shaft NDE too high
TRIPS.T055 | BOOL | VAHH0062Y Vibration motor shaft DE too high
TRIPS.T056 | BOOL | VAHH0050Y Vibration gearbox HS shaft DE too high
TRIPS.T057 | BOOL | VAHH0051Y Vibration gearbox HS shaft NDE too high
TRIPS.T058 | BOOL | TAHH1476 Temperature motor shaft radial bearing DE too high
TRIPS.T059 | BOOL | TAHH1477 Temperature motor shaft radial bearing NDE too high
TRIPS.T060 | BOOL | TAHH1471 Temperature motor winding U too high
TRIPS.T061 | BOOL | TAHH1472 Temperature motor winding V too high
TRIPS.T062 | BOOL | TAHH1473 Temperature motor winding W too high